## Feuil2
Area | Component name | Function | Failure mode | Failure cause | Failure effect - local | Failure effect - global | Failure detection | Other provision | Remark
Color tank | HH sensor | triggers an alarm preventing the filling of the tank | fails to activate | Hardware error | Tank may overflow | Color everywhere, damaging equipment and need for a extended maintenance | Visual (occurs only during filling), analog sensor | Establish visual inspection during the filling of the tank | Critical failure
| H sensor | triggers a warning informing the tank is almost full | fails to activate | Hardware error | No warning on tank reaching maximum capacity | Tank filling may be stopped abruptly | Analog sensor, HH sensor
| L sensor | triggers a warning informing the tank is almost empty | fails to activate | Hardware error | No warning on color level being too low | Color may become unavailable suddenly | Analog sensor, LL sensor, SCADA calculations
| LL sensor | triggers an alarm and an interlock preventing mixes containing this color to be prepared | fails to activate | Hardware error | Tank not providing color | Color mix not accurate | Flowmeter feedback, SCADA calculation
| Analog level sensor | Informs the operator of the color level | wrong output | Hardware error | Inaccurate calculations of tank capacity, wrong maintenance schedule | Loss of productivity | SCADA calculations, digital sensors
| Tank | holds the color | leakage | Contact with object | Tank leaking | Color everywhere, damaging equipment and need for a extended maintenance | Analog and digital sensors, visual inspections | Establish routine inspections | Critical failure
| Valve | releases the color from the tank | fails to open | Hardware error | Tank not providing color | Color mix not accurate | Flowmeter feedback
|  |  | fails to close | Hardware error | Color pouring endlessly into the pipe | Color everywhere, damaging equipment and need for a extended maintenance | Flowmeter feedback | Add a security valve at the end of the color pipe | Critical failure
| Pipe | conducts the color to the mixing tank | leakage | Contact with object | Pipe leaking | Color everywhere, damaging equipment and need for a extended maintenance | Flowmeter feedback, visual inspections | Establish routine inspections | Critical failure
| Flowmeter (valve) | provides feedback from the valve | wrong output | Hardware error | SCADA not providing the real system state | Loss of productivity | SCADA calculations
| Flowmeter (pipe) | checks the amounts of colored poured into the mixing tank | wrong output | Hardware error | SCADA not providing the real system state | Loss of productivity | SCADA calculations
Mixing tank | Mixer | mixes the colors | fails to start | Motor broken | Colors not mixed | Color mix not accurate | Motor feedback | Establish routine inspections
| Analog level sensor | Informs the operator of the color level | wrong output | Hardware error | Inaccurate calculation of mixing time and emptying time | Color mix not accurate, loss of productivity | SCADA calculations, digital sensors
| L sensor | triggers a warning informing the tank is almost empty | fails to activate | Hardware error | No warning on mixing tank being almost empty | Loss of productivity | Analog sensor, SCADA calculations
| H sensor | triggers an alarm and an interlock closing color valves | fails to activate | Hardware error | Mixing tank may overflow | Color everywhere, damaging equipment and need for a extended maintenance | Analog sensor, SCADA calculations | Establish visual inspection during the filling of the tank | Critical failure
| Flowmeter | checks the amounts of colored poured into the end pipe | wrong output | Hardware error | SCADA not providing the real system state | Loss of productivity | SCADA calculations
| Pump | pumps the color mix to the endpipe | fails to start | Motor broken | Mixing tank may not empty correctly | Color mix unavailable | Flowmeter feedback
| Valve | allows the mix to be pumped | fails to open | Hardware error | Mixing tank cannot empty | Color mix unavailable | Flowmeter feedback
|  |  | fails to close | Hardware error | Color pouring without control into the endpipe | Color everywhere, damaging equipment and need for a extended maintenance | Flowmeter feedback | Add a security valve at the end of the color pipe | Critical failure
| Pipe | conducts the color mix to the exit | leakage | Contact with object | Pipe leaking | Color everywhere, damaging equipment and need for a extended maintenance | Flowmeter feedback | Establish routine inspections | Critical failure
| Tank | holds the color mix | leakage | Contact with object | Tank leaking | Color everywhere, damaging equipment and need for a extended maintenance | Analog and digital sensors, visual inspections | Establish routine inspections | Critical failure